## Sheet1
Element | Effluent | [7 empty] | SRT | Biogas |  | Sludge | Aeration |  |  |  | Pumping | [7 empty] | Mixing |  | OPEX
Feature | COD [mg/L] | BOD [mg/L] | TSS [mg/L] | TN [mg/L] | NH4 N [mg/L] | TP [mg/L] | Ortho P [mg/L] | TOC [mg/L] | SRT [d] | CH4 production [kg/hr] | CH4 content [%] | Sludge production [tonne/d] | Liquid aeration flowrate [m3/d] | Sludge aeration flowrate [m3/d] | Liquid aeration energy [kW] | Total aeration energy [kW] | Influent pumping energy [kW] | RAS pumping energy [kW] | WAS pumping energy [kW] | Internal recycle pumping energy [kW] | Permeate pumping energy [kW] | GT underflow pumping energy [kW] | MT underflow pumping energy [kW] | AD pumping energy [kW] | ASR mixing energy [kW] | AD mixing energy [kW] | Aeration energy cost [USD/d] | Pumping energy cost [USD/d] | Mixing energy cost [USD/d] | External carbon cost [USD/d] | Coagulant cost [USD/d] | Lime cost [USD/d] | Lime stablization energy cost [USD/d] | Sludge disposal cost [USD/d] | Total OPEX [USD/d]
B1 | 41.2804 | 9.5233 | 19.7367 | 30.7691 | 4.2097 | 5.6126 | 5.1007 | 14.9736 | 2.0492 | 47.7724 | 57.5058 | 18.9443 | 671658.6482 |  | 561.5089 | 561.5089 | 67.3444 | 28.7686 | 2.4611 | 0 | 0 | 0.34241 | 0.34403 | 0.46323 | 0 | 9.6528 | 1053.8398 | 187.1616 | 18.1164 | 0 | 0 | 0 | 0 | 1297.6841 | 2556.8019
B2 | 41.1417 | 9.5626 | 19.6264 | 25.5063 | 5.0603 | 6.29 | 5.7803 | 14.9236 | 2.0497 |  |  | 7.5162 | 562164.8743 | 449334.2661 | 469.9717 | 956.3755 | 67.3444 | 28.7686 | 2.4611 | 0 | 0 | 0.34241 | 0.33123 | 0 | 0 | 0 | 1794.9256 | 186.2682 | 0 | 0 | 0 | 0 | 0 | 514.8603 | 2496.054
B3 | 41.2995 | 9.6097 | 19.7468 | 24.1249 | 3.5579 | 4.4616 | 3.9512 | 14.9808 | 2.0501 |  |  | 36.5492 | 590869.821 |  | 493.9691 | 493.9691 | 67.3444 | 28.7686 | 2.4611 | 0 | 0 | 0.34241 | 0.34535 | 0 | 0 | 0 | 927.0813 | 186.2947 | 0 | 0 | 0 | 226.5273 | 13.862 | 2503.6189 | 3857.3841
C1 | 27.9726 | 3.55 | 8.153 | 28.8809 | 0.71593 | 5.5445 | 5.2764 | 10.1227 | 2.056 | 35.1605 | 53.3626 | 19.9367 | 882750.8304 |  | 737.9826 | 737.9826 | 67.3444 | 28.7686 | 3.5525 | 0 | 0 | 0 | 0.67001 | 0.40201 | 0 | 9.6528 | 1385.0458 | 189.0642 | 18.1164 | 0 | 0 | 0 | 0 | 1365.6642 | 2957.8906
C2 | 27.8693 | 3.5848 | 8.0821 | 25.7476 | 0.88424 | 6.3081 | 6.0407 | 10.0858 | 2.0562 |  |  | 6.8394 | 766307.4138 | 415724.6184 | 640.6355 | 1090.657 | 67.3444 | 28.7686 | 3.5525 | 0 | 0 | 0 | 0.64618 | 0 | 0 | 0 | 2046.945 | 188.265 | 0 | 0 | 0 | 0 | 0 | 468.5019 | 2703.7119
C3 | 28.0324 | 3.6467 | 8.1335 | 25.1847 | 23.3704 | 4.0012 | 3.734 | 10.1446 | 2.0588 |  |  | 38.2842 | 484201.8478 |  | 404.7944 | 404.7944 | 67.3444 | 28.7686 | 3.5525 | 0 | 0 | 0 | 0.66475 | 0 | 0 | 0 | 759.718 | 188.2998 | 0 | 0 | 0 | 205.7218 | 14.5201 | 2622.4691 | 3790.7289
E2 | 27.5169 | 2.7875 | 7.6701 | 26.7333 | 0.088544 | 6.4906 | 6.2441 | 9.9595 | 6.0758 |  |  | 5.3873 | 517057.7097 | 348550.1544 | 432.262 | 809.5671 | 67.3444 | 28.7686 | 3.641 | 0 | 0 | 0 | 0.53017 | 0 | 0 | 0 | 1519.3956 | 188.2134 | 0 | 0 | 0 | 0 | 0 | 369.0286 | 2076.6376
E2P | 27.7005 | 3.3998 | 7.8919 | 24.4794 | 0.059285 | 5.477 | 5.2154 | 10.026 | 6.0378 |  |  | 20.382 | 417256.4916 | 256917.1191 | 348.8278 | 605.7084 | 67.3444 | 28.7686 | 2.1098 | 0 | 0 | 0.34241 | 0.30278 | 0 | 0 | 0 | 1136.7935 | 185.5555 | 0 | 0 | 0 | 0 | 0 | 1396.1663 | 2718.5153
F1 | 27.8704 | 3.4591 | 8.0059 | 29.9238 | 0.048522 | 5.6126 | 5.3476 | 10.0859 | 6.0367 | 42.1505 | 58.7377 | 19.6767 | 465334.0481 |  | 389.0208 | 389.0208 | 67.3444 | 28.7686 | 2.1098 | 0 | 0 | 0.38708 | 0.30726 | 0.47466 | 0 | 9.6528 | 730.1143 | 186.5385 | 18.1164 | 0 | 0 | 0 | 0 | 1347.8549 | 2282.6241
G1 | 25.3797 | 2.8129 | 8.0076 | 7.6475 | 0.32213 | 0.94671 | 0.10521 | 9.1827 | 10.718 | 41.9238 | 59.1522 | 27.5687 | 325415.8541 |  | 272.0487 | 272.0487 | 67.3444 | 17.8357 | 1.8373 | 90.9084 | 0 | 0.38708 | 0.50266 | 0.5919 | 23.4847 | 10.7884 | 510.5811 | 336.7119 | 64.3238 | 3387.7777 | 0 | 0 | 0 | 1888.4558 | 6187.8503
G2 | 25.2264 | 2.7865 | 8.0074 | 6.3467 | 0.32054 | 1.0323 | 0.15214 | 9.1277 | 10.6407 |  |  | 16.5719 | 296273.2382 | 420549.5845 | 247.6854 | 702.9299 | 67.3444 | 17.8357 | 1.8471 | 89.95 | 0 | 0.38708 | 0.49613 | 0 | 23.4847 | 0 | 1319.2588 | 333.8086 | 44.0761 | 3387.7777 | 0 | 0 | 0 | 1135.1772 | 6220.0983
G3 | 26.5978 | 3.1736 | 8.005 | 7.2471 | 0.49934 | 0.59999 | 0.032092 | 9.6239 | 10.3545 |  |  | 38.3609 | 274824.1604 |  | 229.7539 | 229.7539 | 67.3444 | 17.8357 | 1.8864 | 90.9158 | 0 | 0.38708 | 0.38011 | 0 | 23.4847 | 0 | 431.2021 | 335.4771 | 44.0761 | 1195.6862 | 0 | 237.7833 | 14.5491 | 2627.7225 | 4886.4965
H1 | 21.9648 | 2.783 | 8.0071 | 7.541 | 0.12642 | 1.7589 | 1.3451 | 7.9521 | 10.7078 | 43.5153 | 59.0837 | 25.3646 | 350389.7319 |  | 292.927 | 292.927 | 67.3444 | 17.8357 | 1.4859 | 67.4625 | 0 | 0.38708 | 0.35882 | 0.5056 | 14.3395 | 12.4919 | 549.7654 | 291.6174 | 50.3571 | 1713.8169 | 1708.6678 | 0 | 0 | 1737.4779 | 6051.7025
I1 | 27.1583 | 2.389 | 8.0752 | 5.3313 | 0.27757 | 3.984 | 3.5366 | 9.8311 | 12.684 | 19.703 | 55.376 | 21.2779 | 409682.4881 |  | 342.4959 | 342.4959 | 67.3444 | 28.7686 | 3.2087 | 67.4625 | 0 | 0 | 0.56868 | 0.34121 | 50.3081 | 9.6528 | 642.7963 | 314.7283 | 112.5347 | 0 | 0 | 0 | 0 | 1457.5382 | 2527.5975
I2 | 27.0925 | 2.4424 | 7.9952 | 4.5764 | 0.30486 | 4.9232 | 4.4839 | 9.808 | 12.6879 |  |  | 7.907 | 378752.9097 | 310750.1402 | 316.6387 | 653.0254 | 67.3444 | 28.7686 | 3.2087 | 67.4625 | 0 | 0 | 0.54582 | 0 | 50.3081 | 0 | 1225.598 | 314.045 | 94.4183 | 0 | 0 | 0 | 0 | 541.6316 | 2175.693
I3 | 27.1347 | 2.3923 | 8.0671 | 4.4078 | 0.2529 | 0.99577 | 0.53376 | 9.8225 | 12.7116 |  |  | 32.8011 | 398232.9905 |  | 332.9241 | 332.9241 | 67.3444 | 28.7686 | 3.2087 | 67.4625 | 0 | 0 | 0.5713 | 0 | 46.9013 | 0 | 624.832 | 314.0929 | 88.0243 | 0 | 0 | 175.3903 | 12.4405 | 2246.8787 | 3461.6586
N1 | 19.2477 | 0.61238 | 1.0616 | 5.0794 | 0.11106 | 0.34799 | 0.14403 | 6.9501 | 11.0913 | 49.2245 | 58.1084 | 30.564 | 1320743.6827 |  | 1104.1461 | 1104.1461 | 67.3444 | 89.95 | 2.177 | 112.4375 | 22.4801 | 0.81631 | 0 | 0.61223 | 14.2271 | 13.6275 | 2072.2614 | 555.1905 | 52.2775 | 9964.052 | 0 | 0 | 0 | 2093.6324 | 14737.4138
N2 | 19.0889 | 0.53508 | 0.85092 | 5.1964 | 0.27864 | 0.38272 | 0.21016 | 6.8936 | 6.0612 |  |  | 17.7514 | 1274336.9664 | 429437.7127 | 1065.3499 | 1494.7266 | 67.3444 | 89.95 | 3.3746 | 67.4625 | 22.4843 | 0 | 0.91134 | 0 | 14.2271 | 0 | 2805.3028 | 472.0662 | 26.7014 | 7971.2416 | 0 | 0 | 0 | 1215.9717 | 12491.2837